## Slide 1: Hazards of Electricity
Notes: Highly flammable
Caution explosive atmosphere
Fire, open light and smoking prohibited
Turn off engine and heating
Switch off mobile phones
Engage parking brake
Put gear to parking

## Slide 2: Hazards of Electric Current Electric Pulses
We cannot live without current in our body, as our perceptions are controlled electrically.
Consider the following example, of a thirsty person:
  our eyes see the bottle.
  This perception generates electric pulses in our brain.
  These pulses are transmitted to the muscles via nerves.
  Thus we grasp the bottle with our hand to quench our thirst.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 3: Hazards of Electric Current Electric Pulses
The cardiac muscle also is stimulated by electric pulses.
However, these cannot be controlled by the brain.
The processes in the heart can be made visible by means of an electrocardiogram (ECG).
  Especially the cardiac frequency.
  The curve represents the low frequency of the heart.
  For a grownup, this is around 60 to 80 beats per minute.
Aorta
Left atrium
right atrium
right ventricle
Sine node
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 4: Hazards of Electric Current Electric Pulses
The ECG curve looks completely different from common alternating current (AC).
Alternating current and alternating voltage follow a sine curve.
Alternating current has a frequency of 50 Hz:
  i.e. it changes direction 100 times per second.
  as opposed to a heart frequency of 60 to 80 times per minute.
The following applies for this :
Alternating voltage
Alternating current
Alternating current - alternating voltage
û : peak value of alternating voltage
ueff : effective value
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 5: Hazards of Electric Current Electric Pulses
What is the relation between the frequency of alternating current and the cardiac frequency?
The person touches a part under voltage.
  The current flows through the human body and acts on muscles and nerves.
  With this, the current also flows via the heart and is superimposed with a frequency of 50 Hz onto the pulses of the heart.
Ohm‘s law also applies when current flows through the human body.
With a mains voltage of 230 V, a current of 230 mA is flowing when a body resistance of 1000 Ohm is assumed.
Current flow through the human body
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 6: Hazards of Electric Current Electric Pulses
With this, the abbreviations have the following meanings:
IT = Body Current
UT = Contact Voltage
ZT = Body resistance at 230 V
  Current path hand-hand 1000 
  Current path hand-foot 1000 
  Current path hand-feet 750 
  Current path hands-feet 500 
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 7: Hazards of Electric Current Effects of Electric Current
What happens when electric current passes through the body?
  Physiological effects.
  Perception of pain, muscle cramps.
  Circulatory disturbances, ventricular fibrillation.
Further effects may occur with higher body currents, for example with high voltage.
  Thermal effects
    Burns, coagulation of protein and bursting of blood corpuscles.
  Chemical effects
    Electrolytic decomposition of body fluids, especially in the case of DC.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 8: Hazards of Electric Current Effects of Electric Current
Ventricular fibrillation as a physiological effect
  When alternating current acts onto the heart, ventricular fibrillation or cardiac arrest can occur.
  The heart looses its natural rhythm and no longer works normally.
  On the ECG, this looks as follows:
After three to five minutes, the lacking supply of oxygen to the brain leads to permanent damage or death.
Ventricular fibrillation
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 9: Hazards of Electric Current Effects of Electric Current
Ventricular fibrillation or cardiac arrest can occur under unfavourable conditions.
However, this depends on various factors:
  Magnitude of the amperage.
  Time of duration.
  Current type (DC or AC), frequency.
  Path of the current in the body.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 10: Hazards of Electric Current Dangerous Body Currents
Intensity range 3:
Muscle cramps
Respiratory difficulties
Disturbance of the cardiac rhythm
normally no permanent organic damage is to be expected
Intensity range 2:
0.5 to 2 mA: Current is perceived
3 to 5 mA: Pain perception starts
10 to 20 mA: Let-go-threshold range
normally there is no dangerous current flow through the body
Perception limit
Ventricular fibrillation is probable
Time
[ms]
Current
[mA]
0,1
10
100
1000
10000
50
500
5000
20
200
2000
1,0
10
1000
100
5,0
50
500
2,0
20
200
0,2
0,5
1
2
4
Let-go-limit
from 300 ms up: Cardiac fibrillation is probable
3
from 10 ms up:
Let-go-limit
200 mA
Intensity range 4:
Ventricular fibrillation
Cardiac arrest
Respiratory standstill
Intensity range 1:
No effects – even with any length of the effect duration
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 11: Hazards of Electric Current Dangerous Body Currents
Threshold values for AC 50 to 69 Hz:
  with the tongue  from 4.0 …5.0 A
  With the finger  from 1.0 … 1.5 mA
  Let go threshold (women)  from 6 mA (men)  from 9 mA
  Cramps of the breathing muscles  from 20 mA
  Ventricular fibrillation  from 50 mA
DC is as dangerous as AC
  However, the threshold values for DC are higher. The values described for AC appear with DC only with two to three times higher amperages, except for thermal effects.
From 500 mA on, the current effect always is fatal !!
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 12: Hazards of Electric Current Technical Terms and Characteristic Values
Electric current flow in case of a fault.
The figure shows a defective lamp. The person touches the metal housing, which is under voltage because of an insulation fault (3).
The resulting fault circuit contains some resistances which determine the magnitude of the fault current (body current IK).
The contact voltage UC is another influencing factor.
R
+
-
Ground
RC
UC
RB
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 13: Hazards of Electric Current Technical Terms and Characteristic Values
RL : Line resistance
RF : Fault resistance in the isolation
RC : Contact resistance
RB : Body resistance
RSt : Location resistance
RA : Ground resistance of the installation
RC
UC
RB
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 14: Hazards of Electric Current Technical Terms and Characteristic Values
Investigations have shown that the body resistance RB also depends on the contact voltage UC.
When the contact voltage increases, the resistance of the human body decreases.
Accordingly, IK becomes larger and the danger for the human also becomes larger.
Contact voltage UC
Body resistance RB
Contact resistance RC
Location resistance RST
Body current IB
The body current depends on various factors
Current path from left or right hand to both feet and f  1000 Hz
RB
UC
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 15: Hazards of Electric Current Technical Terms and Characteristic Values
Depending on the path of the current through the body, the value of the body resistance is around 500 Ohm to 1000 Ohm.
Endangering for humans starts after the values listed above at 50 V AC or 120 V DC.
Max. permissible contact voltage
(Alternating current)
(Direct current)
Max. permissible contact voltage with DC and AC
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 16: Hazards of Electric Current Technical Terms and Characteristic Values
Short-circuit, three poles
Short-circuit, single poles
Body contact
Ground fault
Conductor fault
Types of potential short circuits
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 17: Hazards of Electric Current Technical Terms and Characteristic Values
Conductor fault
  Faulty connection between conductors, where there is also a consumer in the fault circuit.
Short-circuit
  Conductive low-impedance connection between conductors with a voltage difference to each other during operation, caused by an insulation fault.
Body contact
  Conductive connection between conductive parts not belonging to the operation circuit and parts under voltage during operation, caused by an insulation fault.
Ground fault
  Conductive connection of an outer conductor with ground or grounded parts. The ground fault can occur via an arc.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 18: Accident Prevention Measures in Case of Accidents
Depending on the amperage, electric accidents cause:
Certain first measures must be taken before the rescue service arrives.
The so-called RESCUE CHAIN starts!
Unconsciousness.
Shock.
Stop of breathing or
Cardiac/circulatory arrest.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 19: Accident Prevention Measures in Case of Accidents
Rescue chain
Life-saving first measures!
Interrupt the accident circuit
Emergency call
First aid
Medical examination
Extended life-saving measures!
Diagnostics
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 20: Accident Prevention Measures in Case of Accidents
The following links of the chain apply for layman helper:
In order for the person who has suffered the accident to survive the electric accidents without consequences, the life-saving first measures must be executed immediately.
Rescue chain
Interrupt the accident circuit
Emergency call
Everybody
Everybody
Life-saving first measures!
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 21: Accident Prevention Measures in Case of Accidents
Persons without first aid training should do only the following:
  Switch off the installation.
  Pull the plug.
  Pull the fuse or trip the breaker.
In no case may the injured person be touched as long as the voltage has not been switched off, as otherwise there is also mortal danger for the rescuer!
Life-saving first measures!
Interrupt the circuit
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 22: Accident Prevention Measures in Case of Accidents
The injured person may be moved out of the danger area only after the current has been switched off.
Life-saving first measures!
Rescue from the danger area
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 23: Accident Prevention Measures in Case of Accidents
Now the emergency physician must be notified as quickly as possible.
Respect the corresponding emergency plans being if force in your installation.
Life-saving first measures!
Emergency call
In Germany
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 24: Accident Prevention Measures in Case of Accidents
The rest of the rescue chain looks like this :
These first aid measures may be executed only by trained first-aid personnel, rescue ambulance men, or physicians
Rescue chain
First aid
Medical exami- nation
Diagnostics
Extended life saving-first measures!
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 25: Accident Prevention Safety Rules
Work on live active parts of electrical installations and equipment is not permitted (except for exceptions).
Before the start of work on active parts, the dead state must be created and it must be insured during the work.
Absence of voltage from neighboring active parts must be created when these:
  are not protected against direct touching,
  are not protected against direct touching by covering or by barriers or,
  when these are not covered during operation of electric equipment.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 26: Accident Prevention Safety Rules
Observation of the five safety rules is
vital !
Five safety rules:
• Disconnect.
• Cover neighboring live parts and provide barriers.
• Grounding and short-circuiting.
• Confirm that there is no voltage.
• Secure against reconnection.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 27: Accident Prevention Safety Rules
However, there are some exceptions for installations with rated voltages up to 1000 V:
In these installations, grounding and short-circuiting is not required when the work place can be made completely dead for example by removal of the fuses.
Five safety rules:
• Disconnect.
• Cover neighboring live parts and provide barriers.
• Grounding and short-circuiting.
• Confirm that there is no voltage.
• Secure against reconnection.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 28: Accident Prevention Safety Rules
Before the start of work, disconnect all lines which can carry voltage to the work place.
1. Safety rule – Disconnect
The absence of voltage by itself is not sufficient proof that disconnection has been made!
The live parts include :
- PDU.
- Drive motor with inverter. - DC / DC - converter for HV.
- Air compressor. - Traction battery with control equipment.
- Air conditioning compressor.
- DI water heater. - all lines “marked orange“!
- Start - up – heater.
- Radiator fan.
- High-temperature pump.
- PTC heater for interior.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 29
PDU
+
FCM
HT pump
Radiator fan
Air conditioning compressor (IC)
PTC-heater for interior
Air compressor BZ
Transverter with motor (IBT)
HV -
HV +
HV-plug with bridge in the plug
left above PCB
Safety circuit
Oscillator
-
PCB
PCB
PCB
HV-DC/DC-
converter
PCB
PCB
H2-
Alarm
BMS with battery
Interlock
-OUT
Safety circuit
Receiver
TCU
EPO IN
Interlock
-IN
+
+
5k6
5k6
DI-water heater BZ
Start-up - heater BZ
5K6
+
5K6
+
EPO-line
5K6
5K6
EPO-OUT
5K6
+
5K6
LV-plug
Battery +
Battery -
Service Disconnect
Interlock-line
Crash-
switched
Service - Disconnect
Pull !
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 30: Accident Prevention Safety Rules
Prevent reconnection (switching on) by marking, blocking, or locking, take plug or key with you.
Fasten prohibition signs securely. (The sign may be removed only by the person who has attached the sign).
2. Safety Rules –
Secure against reconnection
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 31: Accident Prevention Safety Rules
Absence of voltage always must be determined clearly with a voltage tester.
Use only voltage testers which function correctly and which have a measuring range suitable for the installation.
Before determining the absence of voltage, the function of the voltage tester must be confirmed on live parts.
3. Safety Rules –
Confirm absence of voltage
• Two-pole voltage tester up to 1000V according to DIN.
• Multimeter for example FLUKE
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 32: Accident Prevention Safety Rules
Tools, auxiliary equipment, and remaining materials shall be removed from the work place and from the danger area.
Safety measures shall be canceled only when all persons are outside the danger area.
Remove the warning signs.
Finally, inform the person in charge about the completion either in writing or orally with repetition.
Applications of voltage after completion of the work
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 33: Accident Prevention Safety Rules
Set the ignition switch to the position OFF, remove the key, and put it in your pocket.
Service - Disconnect - Pull the plug on the right in the luggage compartment and put it in your pocket.
Attach a sign “DO NOT SWITCH ON ...”.
Use a suitable voltage tester (multimeter for DC) to check for absence of voltage between (+) and (-). The residual voltage is discharged after max. 2 minutes by discharge resistors.
Procedure for “Disconnecting”
Example for Vehicles
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 34: Protective Measures
Body currents can have life-threatening effects onto human and animals.
Thus it must be tried to prevent these body currents in case of a fault by means of protective measures. There are various possibilities for this:
In most cases, only protection against direct contact by means of the basis insulation is provided. This is intended to prevent direct contact with active parts.
Exclusion of electric shock
Contact with live parts is prevented
Protection in case of contact
SELV
PELV
Protection against direct contact
Isolation
Obstacles
Covering
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 35: Protective Measures
The protection against indirect contact must occur in case of a fault of the equipment. With this, no dangerous contact voltage may occur for humans.
The occurrence of a contact voltage is prevented.
The continued existence of a voltage is prevented.
Protective insulation
Potential equalization and grounding
Non-conductive rooms
Protection against indirect contact
Protection isolation
Protection in case of indirect contact
TN system
IT system
Switching off in the TT system
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 36: Protective Measures Protection against direct contact
Protection against direct contact
Complete protection
Protection by insulation of active parts
Protection by covering or sheathing
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 37: Protective Measures Protection against direct contact, complete protection
Insulation of active parts
  Complete protection against direct contact is obtained when the live parts are equipped with operational or basis insulation. Direct insulation of the conductor (operational insulation) shall prevent a conductor or winding fault. Basis insulation protects against dangerous body currents in case of damage to the operational insulation.
Covering or sheathing
  The live parts are covered solidly and securely by insulating materials, so that contact protection is assured (for example by keeping fingers and other objects away).
Operational insulation
Basis insulation
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 38: Protective Measures Protection against direct contact, partial protection
Protection against direct contact
Partial protection
Protection by obstacles
Protection by distance
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 39: Protective Measures Protection against direct contact, partial protection
Protection by obstacles
  These obstacles keep persons from accidentally approaching active parts.
  These obstacles provide only a partial protection, as they can be removed without tools.
Protection by distance
  In this case also, only partial protection is provided. The active parts shall be outside the hand range.
  The min. Distance of 2.5 m to the top and 1.25 m to the side and down limit the hand range.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 40: Protective Measures Protection against direct contact, partial protection
Protection against direct contact
Partial protection
Protection by fault-current circuit breaker (RCD)
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 41: Protective Measures Protection against direct contact, additional protection
Protection by fault-current circuit breaker
  These circuit breaker offer additional protection in case of direct contact when other protective measures fail. These breakers with rated fault currents of 10 mA and 30 mA offer the most extensive protection for humans.
  They shall not be used as the only protection, but only as additional protection.
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 42: Protective Measures Protection against direct contact, additional protection
Function of the fault-current circuit breaker
  The input and output currents are checked in a sum current transformer (magnetic circuit).
  In the normal case, the sum of both currents is zero. Thus no magnetic field is created. In case of a fault, a part of the current no longer flows via the sum current transformer, but flows off via ground (mass). A magnetic field is created and the breaker is tripped.
without a fault
with a fault
Notes: Page <number>
<footer>
<header>
30.07.26

## Slide 43: Protective Measures Protection in case of contact, Protection Low Voltage
The conventional terms like:
  Protection low voltage.
  Functional low voltage.
have been replaced by the following terms:

## Slide 44: Protective Measures Protection in case of contact, Protection Low Voltage
The requirements for SELV circuits are realized by:
  the use of low voltages AC < 50 V / DC < 120 V.
  generation of the voltage by safe isolation.
  not grounded active parts of the SELV circuit.
  Use of suitable plug-and-socket devices.
Connection between two outer conductors
Connection between outer conductor and neutral conductor

## Slide 45: Protective Measures Protection in case of contact, Protection Low Voltage
The requirements for PELV circuits are realized by:
  The use of low voltages AC < 50 V / DC < 120 V
  Generation of the voltage by safe isolation
  Grounded active parts of the PELV circuit
  Use of suitable plug-and-socket devices
Connection between two outer conductors
Connection between outer conductor and neutral conductor

## Slide 46: Protective Measures Protection in case of contact, Functional Low Voltage
The requirements for FELV circuits are realized by:
  The use of low voltages AC < 50 V / DC < 120 V.
  Generation of the voltage by basis separation.
  Grounded active parts of the FELV circuit.
  Use of suitable plug-and-socket devices.
The basis separation of the FELV power supplies is not a safe separation!
These voltage sources are not recognized as a protection class of their own.
Connection between two outer conductors
Connection between outer conductor and neutral conductor

## Slide 47: Protective Measures Protection in case of contact, Low Voltage
Some further possibilities for generation of low voltages are shown here. These are amongst others:
  Safety transformers with safe isolation.
  Transformers with safe isolation.
  galvanic elements (accumulators).
Further possibilities for generation of low voltages

## Slide 48: Protective Measures Protection against indirect contact
The special insulation of the equipment prevents contact with live parts of the equipment in case of faulty basis isolation. Thus a dangerous contact voltage cannot occur.
Types of protection insulation
Full insulation The housing is made of nonconductive material
for exapmle, a coffee maker
Insulating sheathing The metal housing is coated with plastic on the outside.
for example, an electric drill
Insulating lining The metal housing is lined with plastic on the inside.
for example, a meter closet
Intermediate insulation Metal parts extending to the outside are interrupted by insulating pieces.
for example, a drive shaft

## Slide 49: Protective Measures Protection against indirect contact, protective insulation
The basis and operational insulation is reinforced by an additional insulation.
  With this, coating of varnish, anodization, etc. are not permitted.
Operational insulation
Basis insulation
Protective insulation

## Slide 50: Protective Measures Protection against indirect contact, protective insulation
In the figure below, no current flows through the human body as there is no conductive connection to the supply grid.
The reason for this is that the isolation transformer galvanically separates the mains circuit from the consumer circuit, which means that the primary winding has no electric connection to the secondary winding.

## Slide 51: Protective Measures Protection against indirect contact, protection by switching off
With this protective measure, a fault current IF flows from the live conductor via the housing and the protective conductor (mass connection) in case of a fault, and this current trips the circuit breaker. Because of this low-impedance connection of the housing with the so-called neutral point of the voltage source, in the ideal case no contact voltage or only a very low one occurs.
There is no danger to people.

## Slide 52: Protective Measures Protection against indirect contact, protection by switching off
This network type corresponds to that of an electric vehicle. In vehicles, this typically is a DC network which has no connection to the chassis. This means that the minus pole (-) of the network is not connected to the chassis mass.
This is called an isolated neutral point.

## Slide 53: Protective Measures Protection against indirect contact, protection by switching off
A monitoring device constantly checks the insulation resistance between ground (mass) and the live conductors.
In case of a fault, i.e. when either the (-) pole or the (+) pole shows a ground fault (mass fault), the monitoring device switches the vehicle to a voltage-free state because of the smaller insulation resistance.
However, the 12 V vehicle voltage is not influenced by this !

## Slide 54: Protective Measures Protection at Vehicle Level
Which protective measures against dangerous body currents are used on electric an fuel cell vehicles ?
Protection by insulation of all lines and equipment
Types and construction
Protection against direct contact

## Slide 55: Protective Measures Protection at Vehicle Level
Protection by covering
Covering of all live parts of the PDU

## Slide 56: Protective Measures Protection at Vehicle Level
Protection by covering, protection by switching off
ZEBRA-
battery
+
-
HLV
Lid HLV bottom
Lid HLV top
Kl. 30
Main contactor
300 V
Service-Disconnect
12 V
Protection in case of indirect contact

## Slide 57: Protective Measures Protection at vehicle level
Protection by switching off
Interlock
The interlock concept assures that the dangerous voltage is switched off via a relay in the PDU and in the traction battery when a plug is pulled.
This 100 Hz square-wave signal is generated in an oscillator an d is looped over all plug connections. As soon as the receiver in the PDU and the traction battery no longer can recognize the signal, the entire network is switched off.
This can be done by pulling a plug or by a line defect.
PDU
+
FCM
HV -
HV +
HV-plug with bridge in the plug
Left above PCB
Safety circuit oscillator
PCB
PCB
PCB
PCB
PCB
H2- Alarm
Interlock -OUT
Safety circuit receiver
TCU
EPO IN
Interlock -IN
+
+
5k6
5k6
5K6
+
5K6
+
EPO-line
5K6
5K6
EPO-OUT
5K6
+
5K6
LV-plug
Batterie +
Batterie -
Service Disconnect
Interlock-line
Crash- switched

## Slide 58: Protective Measures Protection at vehicle level
Protection by switching off
Insulation monitoring
  The HV potentials are insulated against the vehicle mass (IT network). Even in case of an insulation fault, there is no danger for humans. The insulation monitoring device continuously monitors the insulation resistance against mass and against the 12 V battery voltage. As soon as an insulation fault occurs, the voltage is switched off via the two relays. The residual voltage then discharged within the next 60 s via the discharge resistors of the capacitors.

## Slide 59: Safety Advices
Pull the main plug before opening !
Uninterruptible power supply !
Disconnect before start to work!

## Slide 60: Warning Signs
Warning of explosion-hazardous materials !
Warning of corrosive materials !
Warning of explosive atmosphere !
Warning of toxic materials !
Warning of fire-hazardous materials !

## Slide 61: Warning Signs
Warning of danger from battery !
Warning of hazardous location !
Warning of electromagnetic fields !
Warning of dangerous voltage !

## Slide 62: Prohibitory Signs
Touching prohibited! - Live housing
Switching prohibited !
Mobile phone / radio prohibited !
Off limits to unauthorized !