## Slide 1: Capitolo: 4 Tecnologie dell‘idrogeno
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Chapter 4
Title: Hydrogen-Technology
Level: Basic, intermediate, advanced
Requisites: none
Overall aim
The chapter is to provide an overview of the characteristics and hazards associated with hydrogen.
Content
Characteristics of hydrogen
Hydrogen production and storage
Hazards
Learning outcomes
The student will be able to
  Recognized the hazards associated with hydrogen
Appreciate appropriate storage methods
Identify good safety procedures
Methodology
Lectures, group work, discussion
Schedule
Basic: 4 one - hour – units
Intermediate and advanced: 6 one - hour – units

## Slide 2: Informazioni generali sull‘idrogeno
L’idrogeno è l’elemento più diffuso nell’universo.
L’idrogeno si trova al 1° posto nella tabella periodica degli elementi.
L’idrogeno è l’atomo più leggero e più semplice formato solo da un protone e un elettrone.
L’idrogeno è un gas biatomico (H2) nella sua forma elementare.
Sulla terra l’idrogeno si può trovare quasi esclusivamente legato chimicamente ad altri elementi (in atmosfera l’idrogeno libero è solo una piccola ppm).
  Contenuto idrogeno 11,19 wt%.
  Oltre 1/6 degli atomi sulla crosta terrestre, inclusi gli oceani e l’atmosfera, sono formati da idrogeno.
  Il 99.9855 % di idrogeno è presente nella forma di of 11H.
Idrogeno, l‘elemento più diffuso nell‘universo
Tabella periodica (gruppi principali)
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Hydrogen is the most abundant element in the universe, making up 75% by mass and more than 90% by number of atoms of the known matter. Furthermore, in our solar system it forms the main constituent of the sun and the major gas-planets such as Jupiter, Uranus, and Saturn. In outer space, hydrogen is present in atomic or plasma states. Under terrestric conditions, hydrogen exists as a diatomic molecule (H2). Due to the atomic spin of the hydrogen atom, the hydrogen molecule can form a state with parallel spins (ortho H2) or one with antiparallel spins (para H2) having lower energy. At room temperature hydrogen has an equilibrium content of about 75% ortho hydrogen. When approaching the liquid state, the equilibrium content of lower energetic para hydrogen increases. This must be considered in the energy balance when hydrogen is liquified.
Hydrogen has been discovered in 1766 by Henry Cavendish when treating mercury with acids. A detailed analysis who independently discovered the gas in 1787. He initially called it „combustible air“ However, after discovering water as the combustion product, he renamed it to „Hydrogene“ which means „Water Former“. It is likely that other scientists e.g. Robert Boyle in the 17th century or even before Pracelsus in the early 16th century already generated hydrogen yet could not isolate it as a pure substance.
Due to its relatively simple atomic structure consisting of only one proton and one electron, the hydrogen atom played a key role in understanding the theory of atomic structure and the nature of the chemical bond. Its unique chemical and physical properties gave deep insight into the microscopic understanding of matter.
Due to its light weight, hydrogen can escape from Earth’s gravity making H2 a very rare element in the atmosphere (a few ppm). Its content increases with increasing altitude. Nevertheless, chemically bonded hydrogen is the third most abundant element on the Earth.
There are three different isoptopes of hydrogen known. With about 99.99855% 11H is the most abundant isotope. Deuterium, 21H is present with 0.0145% and the radioactive isotope Tritium 31H is present with 10-15%.
Elemental hydrogen is generated naturally under anaerobic conditions by bacteria or algae. Hydrogen used in technical processes normally is produced from reforming of fossil fuels or electrolytic water splitting.

## Slide 3: Economia dell’idrogeno da rinnovabili, uno scenario
Traffico stradale
Applicazioni
aerospaziali
Fiumi
Oceani
Atmosfera
Acqua di falda
Produzione
energia elettrica
Mercato dell’energia
termica
Petrolchimica
Idrogeno
Chimica
Elettrolisi
Demineralizzazione
Produzione di energia
elettrica da solare,
eolico e idroelettrico
Liquefazione
Air
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Although today hydrogen is produced mainly from fossil sources, in the future hydrogen can be considered as an energy vector allowing electricity generated from solar and wind energy to enter the fuel market for road transport as well as aerospace applications. Furthermore, hydrogen could be used for peak shaving or seasonal energy storage in the electricity market. Additionally, gasification of biomass can provide an additional source of renewable energy for the production of hydrogen.
Production of hydrogen from renewable energies and its use as a fuel in road traffic could decrease the dependency on mineral oil which currently is the dominant source for the production of fuels. Hydrogen produced from renewable energies could also reduce the emissions of CO2 and classical pollutants (e.g. CO, NOx soot) generated by internal combustion engines running on fossil fuels. Fuel cell powered vehicles fuelled by hydrogen can be considered as completely emission free at the point of use. Decentralized electrolyzers located at filling stations or so called home fuellers could provide an option for implementing the early stages of a hydrogen infrastructure.
It has to be taken into account, however, that the implementation of a “hydrogen economy” as shown above must deal with the following key issues:
  Limited volumetric energy density of hydrogen
  Implementation of a new fuel infrastructure
  Limited efficiency for use of hydrogen as energy storage
Other pathways for the conversion of renewable energies into fuels or the storage of electricity for peak shaving and seasonal energy storage might eventually be easier implemented.
Currently, the conversion of biomass to hydrocarbon fuels (e.g. diesel) or methanol are studied intensively. Furthermore, advances in battery technology might allow the implementation of pure electric road vehicles.

## Slide 4: Utilizzo dell‘idrogeno oggi
Idrogeno è
  Una importante materia prima nell’industria chimica.
    Produzione di fertilizzanti.
    Petrolchimica (desolforazione, hydrocracking).
    Industria alimentare (indurimento dei grassi).
    Processi metallurgici (tempera, indurimento, sinterizzazione).
    Semiconduttori (elemento di drogaggio).
Le tecnologie dell’idrogeno esistono già allo stato dell’arte.
  In ogni caso, non come tecnologie energetiche.
  Lo stoccaggio e il trasporto dell’idrogeno sono ben conosciuti.
    1900 utilizzo industriale, ad es. gas per saldature.
      Questo può essere considerato l’inizio dell’era dell’idrogeno!.
    1783-1800 prime applicazioni nelle mongolfiere.
    1898 liquefazione dell’idrogeno (James Dewar).
  Utilizzo nel “gas di città”, contenuto di idrogeno circa il 50% - 60%.
In una futura economia dell’idrogeno del solare l’idrogeno potrebbe essere utilizzato come:
  Combustibile pulito.
  Accumulo stagionaledi energia.
  Trasporto di energia attraverso gli oceani.
  Materia prima per la chimica (“petrolchimica rigenerativa”).
A
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
At the present, approximately 500 billion tons of hydrogen are produced worldwide for a plentitude of applications. Appoximately 310 billion Nm3 per year are produced from the conversion of fossil fuel (natural gas, heavy oil). Approximately 190 billion Nm3 per year are produced as so called byproduct hydrogen mainly from reforming and petrochemical sources. The chemical and metal industry are using hydrogen for more than 100 years in large quantities with a good safety record.
        The most prominent use (~ 50%) is the production of ammonia which later on is mostly converted into fertilizers. About 37% of the hydrogen produced is used in petroleum refining mostly for desulfurization and hydrocracking. Approximately 8% hydrogen is used for the production of methanol, mainly for (MBE) Methyl-tert. ButylEther, a powerful anti-knocking additive to gasoline. However, most of the hydrogen produced is used at the site of production. Only 4% are sold as a technical gas which, to mention only a few examples, is used in the food industry for fat hardening, as an inert gas during metallurgical processes or as a high purity doping gas in the semiconductor industry.
In former times town gas consisting of a mixture of CO and hydrogen was used for public energy service. Today, the use of hydrogen for use in energy technology has almost vanished. Nevertheless, waste and byproduct hydrogen which are not isolated from chemical processes, are also still used to generate process energy.
In the future, hydrogen is considered a viable option to provide clean energy. Hydrogen can be produced from a plentitude of primary energies. Initially, these will be fossil energies such as natural gas or coal. As they become available in large quantities, renewable energies such as surplus electricity from wind- and solar power as well as biomass will be the primary source of energy for hydrogen production.
Hydrogen is an ideal fuel for fuel cells. However, it can also be used in internal combustion engines or gas turbines.

## Slide 5: Dati fisico-chimici dell‘idrogeno (CAS-Nummer 01333-74-0)
Densità (273,15K, 1013mbar): 0.0899 kg/Nm³
Punto di ebollizione (1 bar): -252,8 °C 20.3 K
Energia di evaporazione: 445,4 kJ/kg
Punto di fusione: -259.1°C 14.0 K
Entalpia di fusione: 58.5 kJ/kg
Punto critico: - 240 °C 33 K
Entalpia di transizione Orto/para: 40 kJ/kg
Potere calorifico inferiore: 33,33 KWh/kg = 10.8 MJ/Nm³ = 3.0 kWh/Nm³
Potere calorifico superiore: 39.41 KWh/Kg=12.75 MJ/Nm³=3.5KWh/Nm³
Temperatura di innesco: 560°C
Energia minima di innesco: 0.017 mJ
Limiti di accensione: da 4 a 75 Vol% nell’aria, da 4.9 a 94.0 Vol% nell’ossigeno
Pressione di esplosione, deflagrazione: 7.3 bar in air, 8.0 bar nell’ossigeno
Pressione di detonazione pressione di funzionamento x F.30 (approssimativa)
Limiti di detonazione 18-59 Vol% nell’aria
Temperatura di combustione 29% H2 -> T=2318°C nell’aria
29% H2 -> Tmax=3000°C nell’ossigeno
Quenching gap in aria 0.064 cm
Velocità di fiamma max. 346 cm/s
Emissività di fiamma 0.1
Coefficiente di diffusione 0.061 cm2/s in NTP air
Spinta fino a 9 m/s
Dimensione molecolare 1.8 angstroms
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
At room temperature, hydrogen is a a colorless and odorless combustible gas. It has an extremely low boiling point of 20.3 K. The density of hydrogen (89.9 g/Nm3) is approximately 14 times lower than the density of air. Therefore, hydrogen has a tendency to rise
In the liquid state, hydrogen forms a colorless, non corrosive liquid having a density of 0.0700 g/cm3 which is able to condense or freeze all other gasses except helium. The thermal expansion coefficient of liquid hydrogen is by a factor of 23.4 bigger than that of water. This has to be considered when designing tank systems for liquid hydrogen. When evaporating, 1 l of hydrogen will form approximately 845 l gaseous hydrogen. When evaporating into its own volume, liquid hydrogen will build up a pressure of 172 MPa (1720 bar). The critical temperature of hydrogen is 33 K, above this temperature, hydrogen is present only in the gas phase.
At 14 K, hydrogen is forming a solid phase having a density of 0.0763 g/cm3. Therefore, a slush formed from solid and liquid hydrogen is sometimes used to increase the storage density of hydrogen fuel.
Pure hydrogen is a comparatively stable molecule (Energy of dissociation: 432 kJ/mole). It does not decompose when compressed or heated as it is the case with e.g. acetylene. With oxidants e.g. oxygen or chlorine, hydrogen can form explosive mixtures over a wide range of compositions. Above a temperature of 560 °C, mixtures of hydrogen with air will ignite. At temperatures below, ignition can easily be triggered by sparks or catalytic materials e.g. noble metals or some metal oxides.
From a safety point of view, it has to be considered as a highly inflammable gas (F+) lighter than air. The following labels, risk, and safety phrases apply in Europe:
R12: highly inflammable
S7: Keep container tightly closed
S9: Keep container in a well ventilated location
S16: Keep away from sources of ignition
S33: Take precautions against electrostatic effects

## Slide 6: Produzione di idrogeno
Dal gas naturale e da altri idrocarburi
  CH4 + 2 H2O  CO2 + 4 H2
Dal carbone
  C + H2O  CO + H2
  CO + H2O  CO2 + H2
Dalla scissione dell’acqua
  Con elettrolisi
    acqua
    derivato di elettrolisi cloro-alcalina
  Con ciclo termochimico (ISPRA Mark II)
    700 °C CaBr2 + 2 H2O  Ca(OH)2 + 2 HBr
    200 °C 2 HBr + Hg  HgBr2 + H2
    200 °C HgBr2 + Ca(OH)2  CaBr2 + HgO + H2O
    600 °C HgO  Hg + 1/2 O2
    H2O  H2 + 1/2 O2
A
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Hydrogen is not a primary source of energy it needs to be produced and eventually distributed as a technical product. Today fossil fuels such as natural gas or heavy oil are the most prominent sources for hydrogen production.
Production of hydrogen from natural gas is done by the so called reforming process by reacting methane with water at high temperatures in the presence of a catalyst. The reaction is endothermic (energy consuming).
CH4 + H2O  CO + 3 H2 + 206 kJ/mole
At these temperatures CO will simultaneously react with water according to the water gas shift reaction.
CO + H2O  CO2 + H2 -41 kJ/mole
This reaction is slightly exothermic (energy releasing). At the typical reformer operating temperature of 700 °C, the final gas composition in chemical equilibrium will contain approximately 9% CO. The energy provided for the reforming is provided by combusting some fuel outside the reactor. The process is called steam reforming. Steam reformers can be built in a wide range of power levels starting from a few kW in combined heat and power applicatione up to power levels in the GW range when used in refineries.
When using heavy oil as a primary source of energy, so called catalytic partial oxidation (CPO) is used. In this process hydrocarbons are combusted with oxygen to a gas containing CO, CO2 and hydrogen. The hydrogen content again is upgraded by the shift reaction. Large CPO-reactors are installed in refineries. These reactors are operated with neat oxygen generated on site in order to avoid dilution of the gas by nitrogen from the air. CPO is an exothermic process. If an appropriate amount of steam is introduced to the reactor, heat generation by the combustion reaction and heat consumption by the reforming reaction can be balanced. This process is called autothermal reforming. Similar processes can be operated with coal or biomass as a primary fuel.
Furthermore, hydrogen can be produced by electrolysis, either deliberately by water splitting or as a by-product e.g. during the electrolytic synthesis if chlorine.
Thermal decomposition of water using high temperature sources of heat e.g. from concentrated solar radiation has also been investigated. Several steps are necessary to separate hydrogen from oxygen.
Electrolysis, biomass gasification and thermal water splitting are providing pathways to renewable hydrogen.

## Slide 7: Elettrolisi dell’acqua
H2O  H2 + 1/2 O2
  G(l)25°C = -237,141 kJ/mol  1,23 V
  H(l)25°C = -285,830 kJ/mol  1,48 V
Elettrolisi alcalina.
  Elettrolisi convenzionale.
    Elettrodi largamente distanziati.
    Non uso di catalizzatori dedicati.
  Elettrolisi avanzata.
    Elettrodi sottili usando un sottile diaframma poroso.
    Elettrodi speciali.
    Catalizzatori dedicati.
    Operazione pressurizzata.
Elettrolisi della membrana.
  Elettrolita a membrana polimerica.
Elettrolisi ad alta temperatura.
  Elettrolita a ossidi solidi.
A
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Hydrogen can be produced by the electrolytic splitting of water. Due to the usually high cost of electricity, electrolysis is used mainly when comparatively small amounts of hydrogen are needed e.g. for the de-oxidation of boiler water, welding or other metallurgical processes. Nevertheless, when cheap electricity is available e.g. at the site of remote hydro power plants large electrolyzers have been built in order to provide hydrogen for fertilizer (ammonia) production. Less than 1 billion Nm3 of hydrogen per year are currently produced by electrolysis.
In an electrolyzer, electric current is passed through a suitable electrolyte (e.g. potassium hydroxide soulution, sulfuric acid, polymer electrolytes etc.). Since electricity is carried in electrolytes by so called ions, these have to be generated at the electrodes forming the interface between the electric circuit and the electrolyte. At the negative electrode, water is decomposed forming hydrogen, in parallel, oxygen is formed at the positive electrode. Electrolyzers can be made for a large range of power inputs ranging from a few Watts well into the Megawatt range.
In order to split water, input of energy is required. The voltage required to split water (1.48 V) can be calculated directly from the enthalpy of formation (-285.83 kJ/mole). Typically electrolyzers are operated at a cell voltage ranging from 1.8 V to 2 V resulting in a volatge efficiency in the range of 75% to 802%. Additional losses are encountered by auxiliary equipment such as pumps, controls or safety equipment. In large electrolyzers, the losses caused by auxiliaries are having a less severe impact on the overall energy efficiency. Typically, the overall efficiency of small electrolyzers having a power consumption of a few kW ranges between 50%-65%. Large electrolyzers in the MW range are showing overall efficiencies in the range from 60%-75%.
In many cases, an aqueous solution of potassium hydroxide (KOH) as an electrolyte. Such electrolyzers are available over the whole range of the power spectrum. Classsically, perforated nickel electrodes were used as electrodes at ambient pressure. The electrodes had a gap of several millimeters. A micro porous separator was used to separate hydrogen from oxygen. Advanced designs are using hydrodynamically optimized catalyst coated electrodes and minimized electrode distances. Furthermore, the electrolyzer is operated at elevated pressure.
Recently electrolyzers using polymer electrolyte membranes and noble metal catalysts have been developed for hydrogen generation up to a power input of a few hundred kW.
High temperature electrolysis using ceramic electrolytes has been studied extensively for efficiency reasons, however no commercial electrolyzers have been developed to date.

## Slide 8: Metodi di stoccaggio dell‘idrogeno / Condizioni
Idrogeno in pressione:
  Stoccaggio a temperatura ambiente.
  200-700 bar.
Idrogeno liquido:
  Stoccaggio a -253 °C.
  1-5 bar.
Idruri metallici:
  Temperatura ambiente.
  10 bar (50 bar).
  (idruri ad alta temperatura fino a 300 °C).
Source: GfE / HERA
Fonte: Dynetec STORHY
Fonte: Magna Steyr STORHY
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Hydrogen fuel has a high specific energy of 33.33 kWh/kg (~12 MJ/kg) however only a very limited energy density of 3 kWh/Nm3 (10.8 MJ/Nm3). Therefore, hydrogen can be considered as a lightweight but bulky fuel. Efficient storage and transport of hydrogen are thus a key issue for use of hydrogen as a fuel in road traffic. Three major pathways for hydrogen storage are currently pursued.
    Storage of hydrogen as a compressed gas at elevated pressure
    Storage of hydrogen as a deep cold liquid
    Storage of hydrogen as a metal hydride
Due to the form factor all state of the art hydrogen storage systems require large free volume inside the vehicle. New designs for storage vessels are currently under development.
Compressed gas storage
The most well known way of hydrogen storage is in the form of a compressed gas. Currently steel cylinders having a filling pressure of 200 bar or 300 bar are available from almost any supplier of technical gasses. Due to the heavy weight, steel cylinders are not well suited for use in vehicles. For this reason carbon fiber reinforced composite cylinders have been developed. Compressed gas tank systems using carbon fiber reinforced composites are state of the art in natural gas powered vehicles. For hydrogen storage, these cylinders are commercially available for a pressure up to 350 bar. Cylinders having a filling pressure of 700 bar are available as prototypes and are currently being evaluated in demonstration vehicles. Tank systems made from composite cylinders are containing also pressure reducers and safety devices. Compressed gas cylinders can be considered as permanently gas tight.
Liquid hydrogen storage
Liquid hydrogen storage requires high quality thermal insulation of the storage container. This can be achieved by vacuum insulation and multi layer radiation shielding. Nevertheless, evaporation of hydrogen in phases of standstill cannot be avoided completely. Therefore, liquid hydrogen storage tanks cannot be considered as permanently gas tight.
Metal hydride storage
Hydrogen does react with different mainly nickel based alloys to form so called metal hydrides. These materials can adsorb and desorb hydrogen even at room temperature. However, the storage capacity of nickel based alloys is limited. Recently new Mg-based and Al based alloys have been discovered. However, exchange of hydrogen takes place only at elevated temperature in these alloys.

## Slide 9: Schema di un sistema di stoccaggio per idrogeno compresso
Fonte: DaimlerChrysler
To Fuel Cell System
Filling Line Connector
Pressure Relief Line
I
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
High specific energy (kWh/kg) and high energy density (kWh/l) is a prerequisite for use of a hydrogen storage technology in vehicles. Nevertheless, reliability, ease of operation, and safety issues need also to be considered.
        Despite disadvantages in specific energy and energy density, compressed hydrogen storage is most widely used for vehicle application. This is mostly due to the comparatively easy and fast process of refilling compressed hydrogen storage cylinders. Fuelling of liquid hydrogen tanks needs handling of bulky tank nozzles and hoses or the use of a fully automated tank robot. Furthermore, there is no need for hydrogen venting due to evaporation losses in compressed hydrogen storage.
All individual components of the tank system are pressure steady and certified. The pressure regulator provides protection in case of fire by a thermal fuse opening at elevated temperature (e.g.109 °C). The high pressure cylinders can also include solenoid valves to shut of the hydrogen supply to the outside. The tank system contains a high pressure filling connector. In case of external pressure failure, a relief valve protects the tank system from bursting. Excess flow valves are normally used to prevent the release of gas in case ob major leaks in the external piping. Furthermore, check valves are implemented to be able to close of individual cylinders from the filling line and to close the defuelling line. High pressure piping and low pressure piping is separated and clearly marked. Furthermore, temperature and pressure sensors can be included in the hydrogen storage system.
The general design of a compressed hydrogen storage system can be adapted from proven installations in natural gas powered vehicles. In Germany, VDTUEV 757 gives guidelines for the design and approval of gas storage systems. This technical rule requires that the gas storage system must not be installed in the engine compartment nor in the passenger compartment or any other closed space including the trunk. All parts of the gas storage system must be well secured against the effects of acceleration and breaking. The gas storage system must be sufficiently protected from mechanical and corrosive damage.
The gas storage system needs an approval of a notified body. In case of modifications a re approval is required. Maintenance work shall only be carried out by qualified and trained personnel. Regular inspections of the gas storage system are required.

## Slide 10: Gestione dell’idrogeno
Limitazioni:
  Non esiste un solo metodo generale di affrontare il problema sicurezza con l’idrogeno.
  Ognuno deve usare il buon senso.
Cosa sono i “rischi dell’idrogeno”:
  Un pericolo: evento o condizione che può recare danno.
  I punti principali per l’idrogeno sono:
    Pericolo di combustione (valida per tutti i gas combustibili).
    Pericoli di pressione (validi per tutti i contenitori pressurizzati).
    Pericoli di bassa temperatura in caso di idrogeno liquido.
    Pericoli per la salute (nel caso dell’idrogeno principalmente asfissia).
    Pericoli di infragilimento a causa dell’idrogeno.
Rischi:
  Pericolo moltiplicato da eventi imprevisti.
ustioni criogene di 3° grado
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
For safety considerations, it has to be considered that hydrogen is a colorless and odorless flammable gas lighter than air. Due to its small molecular size (1.8 Å), it has
  a low viscosity,
  can pass through openings too small for helium,
  will pass through porous materials,
  can penetrate softgoods, and
  can penetrate intermolecular spaces and grain boundaries in metals (hydrogen embrittlement)
Hydrogen has a high diffusivity, it will rapidly be distributed in confined spaces. Furthermore, it shows a high buoyancy causing hydrogen concentration under the ceiling.
The most serious hazard of hydrogen is its high flammability when mixed with air. Hydrogen forms combustible mixtures with in the range of 4% to 75% hydrogen content. These mixtures are easily ignited, e.g. by open flames, hot surfaces, sparks or catalytically active materials. Hydrogen flames can penetrates very small gaps, which has to be considered when designing or using flame arrestors.
        When burning, the hydrogen flame is mainly emitting ultraviolet light. Therefore, it is invisible to the human eye and due to the very low emission in the infrared spectral range, it is also invisible to infrared based heat sensors or imaging devices.
        Severe thermal burns can occur upon direct contact with the flame. Additionally, harm to skin and eye are expected from UV-exposure. Impurities in hydrogen (carbon, sodium, etc.), however, give color to the flame. In such cases, thermal energy radiated from the flame can lead to flash burns.
        Excessive spill of liquid hydrogen to unprotected body parts can cause hypothermia and severe cryogenic burn (frostbite).
2nd degree thermal burns

## Slide 11: Sicurezza nello stoccaggio di gas idrogeno compresso
I serbatoi per lo stoccaggio di idrogeno compresso vengono rigorosamente testati dal punto di vista della sicurezza:
  Test su materiale grezzo.
  Test di corrosione.
  Test di scoppio.
  Test di ciclicità (ambiente e temperature estreme).
  Test sulle perdite prima della rottura.
  Test sull’esposizione chimica.
  Test di infiammabilità (bonfire).
  Test di penetrazione (bullet).
  Test di tolleranza del flusso del composito.
  Test di rottura da sforzo accelerato.
  Test da impatto (drop).
  Test sulle perdite.
  Test di permeazione.
  Prove di torsione.
  Test sul ciclo dell’idrogeno.
Cilindri di tipo 4
Fonte: Dynetec, STORHY
A
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Compressed gas storage cylinders are subject to a variety of safety tests.
        For lightweight, high pressure storage normally, fully wrapped cylinders with metallic liners (type 3) or fully wrapped non load carrying (plastic) liner (type 4) designs are used. For type approval, it can be assumed that cylinders with metal liners are impermeable to hydrogen, furthermore, it can be assumed that the neck of the liner cannot be sheared from the body easily. Therefore, additional tests are required for type 4 cylinders.
        Since the temperature of hydrogen increases during filling of the tank, cylinders having metallic liners can be considered advantageous regarding the final temperature of a fast filling cycle as well as the time required for the cylinder to reach ambient temperature again.
During burst tests the cylinder is pressurized at a rate < 1.4 MPa/s at ambient temperature. It has been observed that the burst pressure is above the 2.35 fold design pressure.
Pressure cycling tests using a liquid medium in the range from 2 MPa to 1.25 fold working pressure revealed that no leak occurred at 3 times the filling cycles, the cylinder was designed for.
In the chemical exposure test, a ´cylinder with pre-damaged wrapping has been exposed to five chemicals(19% sulfurc acid, 25% sodium hydroxide, 5% methanol in gasoline, 28% ammonium nitrate solution, 50% methanol in water), 5000 cycles to 1.25 fold working pressure, and a 24 h test at 1.25 fold working pressure. The burst pressure was reduced to 1.8 times the working pressure.
In the bonfire test, the cylinder was pressurized to the working pressure with hydrogen. The fire source length was 1.65 m. The cylinder did not burst, however, hydrogen was vented through the built in pressure relief device.
During the penetration test, the cylinder was pressurized with gas and an armour piercing bullet (7.62 mm) was fired at an angle of 45°. The cylinder did not burst, however gas veted through the entrance and the exit opening.
Eventually, the compressed gas storage cylinders passed the requirements for a type approval for on board storage of compressed hydrogen in vehicles.
* Typical for200 bar cylinders
Source: Dynetec

## Slide 12: Limiti / energia di accensione
Prerequisiti per l’accensione dell’idrogeno e per altri gas combustibili:
  Miscela appropriata di idrogeno / gas combustibile nell’aria / ossigeno.
  Fonte per l’accensione (scintilla, valvole, punto incandescente, etc.).
  Energia sufficiente per l’accensione.
C’è un limite minimo e massimo per l’accensione:
  Limite minimo di accensione: valore minimo di H2 in aria / ossigeno.
  Limite massimo di accensione: valore massimo di H2 in aria / ossigeno.
I limiti di accensione dipendono da:
  Temperatura.
  Pressione.
Dopo l’accensione ci sono molte possibilità:
  Deflagrazione.
    velocità di reazione inferiore alla velocità del suono.
  Detonazione.
    Velocità di reazione superiore alla velocità del suono (compressione supersonica).
    Onda d’urto che comprime e surriscalda la miscela di gas.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Despite being a flammable gas, hydrogen is a very stable molecule. It does not decompose by itself as it is the case with acetylene or organic peroxides. A tank filled with pure hydrogen cannot explode even when there is sufficient ignition energy available, since no oxygen is present. However, when hydrogen is mixed with an oxidant such as oxygen (air) or chlorine, this mixture is reacting vigorously when ignited. In order to start the reaction, all elements o the fire triangle must be present simultaneously in appropriate amounts:
  Fuel (hydrogen as a combustible substance)
  Oxidant (e.g. air in sufficient amount)
  Ignition source (e.g. open flame, static discharge, catalyst, ionizing radiation, striking or sparking metal parts etc.)
When dealing with combustion, one can differentiate:
Flames: Flames are ranges of burning or exothermally (by release of heat) reacting gasses or fumes which typically are also a source of visible radiation. (Attention: hydrogen flames are frequently invisible.
Fire: In the case of fire, one has to differentiate useful fires, in which the combustible material burns as desired and harmful fires where the burning of materials is not intended.
Blaze: A blaze is by definition a harmful fire which got out of control
For each fuel, there is a lower and an upper ignition (explosion) limit. The lower ignition limit defines the minimum amount of fuel which needs to be present in a combustible mixture. The upper ignition limit defines the maximum amount of fuel to still form a combustible mixture. Fuel concentrations below the lower ignition limit and above the upper ignition limit do not form combustible mixtures. The ignition limits are further depending on the temperature and the pressure of the mixture.
If the combustible mixture is burning fast, however, at a velocity below the speed of sound, it is called a deflagration. In some combustible mixtures, the reaction front propagates at supersonic speed pushing a shockwave which is compressing and pre heating the gas mixture in front of the reaction front. This is called a detonation.

## Slide 13: Campo di esplosività H2/Aria in base alla diluizione
Da: V. Schröder, BAM Forschungsbericht 253 (2002)
Air / mole%
Explosive mixture
H2 / mole%
N2 / mole%
H2-content / mole%
Temperature / °C
H2-content / mole%
Initial Pressure / bar
Dipendenza da temperatura
Dipendenza da pressione
A
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
The most striking hazard when handling hydrogen is the formation of explosive mixtures of hydrogen and air.
        The effect after igniting combustible mixtures of hydrogen and air is strikingly different if a mixture close to the lower explosion limit is ignited or if a mixture close to the upper explosion limit is ignited.
        When an hydrogen / oxygen mixture close to the lower explosion limit (5.5% H2 in oxygen) is ignited, deflagration (fast propagating flame) occurs with a rather mild pressure increase factor (1.34 bar). The maximum pressure is building up over approximately 1.12 seconds. The fastest pressure rise (2.7 bar/s) is experienced at 0.62 sec after ignition.
        If a mixture close to the upper explosion limit is ignited (93.5% H2 in O2), a sharp increase of pressure (568 bar/s @ 0.056 s after ignition) is observed. The pressure increase factor amounts to 4.92. The maximum pressure is reached 0.09 sec after ignition.
        From these considerations, it is obvious that flammable hydrogen-air mixtures are reacting more vigorously close to the upper ignition limit.
The boundaries within which flammable mixtures are forming are depending on the temperature and the pressure of the gas mixture. The flammability range of hydrogen-air mixtures is widening on “both sides” with increasing temperature. When increasing the pressure, the lower flammability limit is increasing with increasing pressure reaching >5% hydrogen in air at approximately 50 bar. A further increase in pressure does no longer effect the lower flammability limit. The pressure dependence of the upper flammability limit is not uniform. It decreases initially to approx. 71% at a pressure of approximately 10 bar. After that, it increases to 74% at a pressure of 50 bar. From there, a slight decrease with increasing pressure is observed.
A proven way to mitigate explosion hazards is the dilution with inert gasses. Nevertheless, it has to be noted, that a wide range of flammable mixtures is shown in ternary mixtures of hydrogen, air and an inert gas. Therefore, it is mandatory to make sure that storage vessels are containing < 1% hydrogen when they are to be filled with air or < 1% oxygen, when they are to be filled with hydrogen.
Time / sec
Pressure / bar
Time / sec
Pressure / bar
Time / sec
Pressure / bar

## Slide 14: Inertizzazione di contenitori con H2
1. Diluizione con gas inerti:
  Miscela di gas inerti con H2 a basso livello di pressione.
2. Variazioni di pressione (pressure swing):
  Pressurizzazione con gas inerti dopo l’espansione a 1-2 bar.
3. Dislocazione:
  Tipica applicazione in tubi senza strumentazione e raccordi. I gas inerti fanno uscire H2 e altri gas nocivi dai tubi.
Raccomandazioni
In recipienti, strumenti contenenti volume morto usare sempre il metodo “pressure swing”.
Per usi pratici, usare minimo 5 cambi di gas inerti prima di riempire una tanica con idrogeno combustibile (o aria).
Il metodo di dislocazione è raccomandato solo quando i contenitori dalla forma semplice e con un elevato rapporto lunghezza/diametro (es. i tubi) devono essere inertizzati. La dislocazione è più efficiente quando il gas da dislocare ha una densità diversa dal gas utilizzato per l’operazione.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
  Dilution of dangerous i.e. flammable gasses with inert gasses (iertization) is a proven method to avoid the hazards related to handling i.e. combustible mixtures of hydrogen and oxygen.
  By the flushing method, the gas to be removed is diluted by a larger volume of inert gas and thus flushed out of the storage vessel. The diagram to the left is giving an indication how often the gas volume needs to be exchanged in order to achieve “inertization”.
  Please note: The flushing method is typically used at low pressure only. It is not recommended when complicated tank or piping arrangements need to be inertized.
  The following example does describe the process of inertization an air filled storage vessel, i.e. the oxygen content inside the vessel shall be reduced to less than 1 Vol% before filling with a flammable gas, i.e. hydrogen.
1.) Find the concentration of the gas to be removed at the abscissa of the diagram (here 21%).
2.) Move vertically to the line representing the desired residual concentration (here 1%).
3.) Move horizontally to the ordinate and read the minimum “number of gas changes” required (here 3.1 gas changes). The number of gas changes multiplied by the storage volume represents the inert gas volume required for inertization by the flushing method.
Normally, one would use a volume equivalent to 5 gas changes, to account for small dead volumes in the storage system.
For subsequently filling the tank with hydrogen by the flushing method one would reduce the inert gas concentration to less than 0.1%.
In this case one starts at 100% (N2 to be removed), moves vertically to the 1% line and subsequently horizontally to the ordinate. The minimum number of gas changes is 4.7.
Please note: The dilution method is not recommended if in complicated storage systems “shunted flow” is possible e.g. by branches in pipes etc.
Number of gas changes
1 2 3 4 5 6 7 8 9 10
1 2 3 4 5 10 20 30 50 100
 Initial concentration of gas to be removed
residual content desired
1.0 %

## Slide 15: Il metodo “pressure swing“
Quando si rende necessaria l’inertizzazione di sistemi complessi di serbatoi per lo stoccaggio e dei tubi, è raccomandato l’uso del metodo “pressure swing”.
Il metodo “pressure swing” consiste nelle seguenti fasi:
  Diminuire la pressione del contenitore per essere inertizzato all’ambiente.
  Pressurizzare il contenitore da inertizzare con gas inerti e consentire la miscela dei gas.
  Diminuire la pressione nell’ambiente.
  Ripetere i “pressure swings” fino a che la concentrazione dei gas inerti è raggiunta.
  Regola pratica:
  Un numero maggiore di oscillazioni a bassa pressione permette una migliore inertizzazione di un minor numero di oscillazioni ad alta pressione usando lo stesso volume di gas inerte.
I
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
When considering a pressure up to 10 bar, most gasses can be treated as so called “ideal gasses” following the “ideal gas law”.
      pV = nRT
        p: pressure V: Volume n: number of moles of gas R: gas constant (8.314 JK-1mole-1) T: temperature in K
In an ideal gas, the particles (atoms/molecules), the gas is consisting of have no volume of their own and do not interact with each other i.e. show no attractive or repulsive forces.
The ideal gas law states that the number of atoms/molecules of an ideal gas in a given volume at a given pressure and temperature is independent of the nature of the gas.
If a given volume containing a gas to be removed (i.e. hydrogen at atmospheric pressure) is pressurized to a final pressure of 2 barabs with an inert gas (i.e. nitrogen) and subsequently released to 1 barabs, the residual hydrogen concentration is reduced to 50%. A second pressure swing to 2 barabs results in a H2-concentration of 25%, the third to 12.5%, the fourth to 7.25%, the fifth to 3.63%, the sixth to 1.82% and the seventh to 0.91%. One can assume that after 7 pressure swings to 2 barabs requiring 7 times the container volume of inert gas, the storage container is inertized.
When using pressure swings to e.g 5 barabs, the following situation occurs:
After the first swing to 5 barabs, the H2-concentration is reduced to 20%. The second pressure swing to 5 barabs reduces the H2 concentration to 4% and the third pressure swing to 5 barabs reduces the H2 concentration to 0.8%. In this case, the container is inertized after 3 pressure swings to 5 barabs, requiring, however, 12 times the container volume of inert gas.
In case the oxygen content of an air filled container needs to be reduced to less than 1% by the pressure swing method to 2 barabs, the first pressure swing reduces the concentration to 10.5%, the second to 5.25%, the third to 2.6%, the fourth to 1.3% and the fifth to 0.75%

## Slide 16: Rischio di pressione
Il pericolo legato alla pressione può insorgere dalla necessità di stoccare idrogeno con la maggiore densità di energia possibile.
Il pericolo per la pressione può manifestarsi da:
  Improvvisa perdita di gas compresso:
    Sovrappressione.
    Onde d’urto.
    Frammentazione.
  Cambio di fase da liquido a gas.
  Contenitori di idrogeno per stoccaggio troppo pieni.
  Sistema di pressurizzazione non funzionante.
  Sistema di rilevamento pressione non funzionante.
  Sfiato inadeguato.
  Fiamma o surriscaldamento da fonte esterna.
  Esplosioni chimiche.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Sudden release of pressure to the human body can result in bodily harm, injury or even death. This can be caused by the impact of a shockwave on the body or by the impact of fragments from bursting containers or pipes.
The effects of pressure to the human body are dependent on the distance from the site of pressure release, the time of impact, and the local situation. The following table shows the effect of the impact of a shockwave on the human body:
Maximum overpressure Effect
7 kPa 70 mbar 1 psi Knocks a person down
35 kPa 350 mbar 5 psi Eardrum damage expected
100 kPa 1000 mbar 15 psi Lung damage
240 kPa 2400 mbar 35 psi Threshold to fatalities
45 kPa 3450 mbar 50 psi 50% fatalities
450 kPa 4500 mbar 65 psi 99% fatalities
Shockwaves can result from deflagration or detonation of flammable mixtures or by the burst of pressurized storage containers. In general, it can be expected that the intensity of a shockwave originating from a bursting container or pipe decreases with the third power of the distance to the origin.
Bursting gas storage vessels are very dangerous even if their content is neither toxic nor flammable!
For safe operation of pressurized containers, it is mandatory to make sure, the container is certified for the gas to be filled as well as the filling pressure and the certificate is still valid at the time of filling..
In case of fire in the vicinity of a pressurized storage vessel for gasses, make sure to cool the storage vessel e.g. by spraying it with water from a safe distance.

## Slide 17: Rischio di asfissia
L’ossigeno è essenziale per il metabolismo del corpo umano.
  L’aria nell’ambiente ha un contenuto d’ossigeno (O2) di 21 Vol% in azoto (N2) un gas inerte.
  Ad un contenuto di ossigeno inferiore a 15 Vol%, la capacità di un uomo di lavorare è ridotta.
  Ad un contenuto di ossigeno inferiore a 10 Vol%, le persone possono perdere conoscenza.
  Ad un contenuto di ossigeno inferiore a 6 Vol%, la morte può subentrare in pochi minuti.
L’asfissia è causata dalla mancanza di ossigeno nell’atmosfera.
  Idrogeno.
  Gas inerte.
Il corpo umano non rileva la mancanza nell’atmosfera.
L’asfissia può sopraggiungere improvvisamente senza alcun tipo di preavviso.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
The danger of asphyxation is often encountered in close space in the vicinity of leaking gas pipes or when liquefied gasses (e.g. nitrogen (N2) are spilled in a confined space. (One liter of liquefied gas evaporates into 600 to 800 liters of gas!)
If inert gasses containing less than 1% oxygen are inhaled, already the first breath can lead to unconsciousness and even death.

## Slide 18: Regole generali della NASA per la manipolazione dell’idrogeno
Prevenire dispersione di idrogeno.
Sorvegliare costantemente per rilevare perdite accidentali, e prendere dovuti provvedimenti.
Prevenire accumuli di idrogeno disperso attraverso una buona ventilazione.
Eliminare cause e fonti sospette di possibili messe in funzione.
Garantire operazioni in sicurezza sui sistemi criogenici, test periodici sulle perdite e controlli di torsione sulle giunzioni flangiate.
Ricordarsi sempre che l’idrogeno è sempre presente!
  Verificare, il sistema è stato purificato a meno di 1% durante la manutenzione sul sistema.
Ricordarsi sempre che l’ossigeno è sempre presente!
  Verificare, il sistema è stato purificato ad un livello appropriato prima che l’idrogeno venga reintrodotto nel sistema.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
From a safety point of view, hydrogen is nothing but a “flammable gas lighter than air”. In addition, it is colorless and odorless. Therefore, all common safety precautions handling flammable gasses lighter than air should be taken for hydrogen as well. Since odorization e.g. by sulfur containing compounds as it is common in natural gas or LPG is not an option for hydrogen intended for use in fuel cells, due to the sensitivity of fuel cell catalysts to contamination.
If release / leaking of hydrogen has to be considered, the use of hydrogen detectors either mounted inside the room where hydrogen can be released or carried by the person is highly recommended. However, most detectors for hydrogen are cross-sensitive to other combustible gasses such as methane or CO. Normally, hydrogen detectors should cause an alarm as soon as the hydrogen concentration exceeds 0.8% in air (20% of the lower flammability limit of approx. 4% H2 in air). It is mandatory to verify the calibration status of hydrogen sensors on a regular basis.
The density of hydrogen (0.0899 kg/Nm³) is considerable lower than the density of air (1.293 kg/Nm3). When hydrogen is released into air, it has a natural tendency to rise. Therefore, escape of hydrogen at the top of the room must be possible either by active ventilation or by appropriate openings in the ceiling. It has to be taken into account that hydrogen can accumulate in confined space. If hydrogen accumulated at the top of a room cannot escape, it eventually will be distributed inside the entire room by diffusion.
Please be aware that mixtures of hydrogen and pure oxygen (density 1.429 kg/Nm3) can, depending on the concentration, be more heavy than air and will thus “fall” to the bottom of the room forming extremely dangerous oxygen rich flammable mixtures. In case H2/O2 mixtures are handled, the installations in the room need to be explosion proof.
It is well known that hydrogen has wide flammability (explosion) limits, particularly the upper explosion limit (75%) is extremely high. However, in most cases when hydrogen is released to the atmosphere, the lower explosion limit (4%) is more relevant (Methane ~ 5%). However, the lower detonation limit of hydrogen (18%) is above the value observed for methane (~6.3%).
In general, it is mandatory to handle hydrogen only in well ventilated rooms and to avoid ignition sources. Please note that electrical installations are potential sources of ignition.

## Slide 19: Come maneggiare l‘idrogeno con sicurezza
Il rilascio (anche veloce) di puro idrogeno non genera elettricità statica. Comunque esiste il potenziale pericolo nelle seguenti circostanze:
  Legato a particelle.
  Flusso di 2 fasi.
  Flusso liquido.
Nel caso di una scintilla (es. da una scarica elettrica), l’accensione può attivarsi!
Quindi:
  Non rilasciare idrogeno pressurizzato ad alta velocità!.
  Non rilasciare mai idrogeno pressurizzato liberamente all’interno di un edificio!.
Nei siti di potenziale rilascio di idrogeno, aree sufficientemente grandi devono essere definite come “zone pericolose” (pericolo di esplosione).
Introdurre idrogeno solo in contenitori o tubi quando il contenuto di ossigeno residuo è inferiore all’ 1 %.
Inertizzazione di contenitori idrogeno liquido esclusivamente con elio.
In Germania: rispettare l’area e la distanza di sicurezza secondo TRB 610 and BGV 6 (gas).
I
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Upon expansion of hydrogen at room temperature (isenthalpic expansion, Joule-Thomson-Process) there is a temperature increase rather than a temperature decrease as observed in most other gasses (air, nitrogen etc.). Expansion of hydrogen leads to a temperature decrease only below 193 K. Therefore, hydrogen has to be cooled before liquefaction.
Can the temperature increase upon expansion at room temperature be potentially hazardous? (e.g. upon breaking valves)
  Even in an ideal Joule-Thomson-process hydrogen expansion from a 200 bar cylinder to atmospheric pressure leads to a temperature increase of only 6 K.
  This theoretical value is normally not observed in the real world.
  Heating of hydrogen by Joule-Thomson-Effect does obviously not lead to ignition of hydrogen!
  However! Upon release, hydrogen can hit fine metal or metal oxide powders (rust). These cold be catalytic sources of ignition!
In general, facilities and operating procedures must be designed to avoid liberation of hydrogen in dangerous quantities.
  Installations must be technically leak proof due to construction, continuous surveillance and maintenance.
  Escape of hydrogen caused by ordinary operation must be limited to a minimum.
  Upon escape of hydrogen it must be made sure that it
    can escape without causing danger or
    can be drained or disposed of without causing danger.
What‘s the meaning of „technically leak proof“?
Installations, parts of installations and equipment including all disconnectable and permanent joints need to be sealed with respect to the surrounding atmosphere to an extent that fire, explosion and any other hazard to health can not arise.

## Slide 20: Idrogeno: pericolo e tossicologia
Possibile pericolo
  Gas compresso, altamente infiammabile.
  Più leggero dell’aria, si accumula sul soffitto.
  Le miscele di idrogeno-aria possono essere (sono) esplosive.
  A velocità elevata di fuga, pericolo di autoaccensione da fonti catalitiche di innesco (es. da trafilamento).
  Possibile accensione o esplosione da contatto con forti ossidanti.
  Alte concentrazioni di idrogeno possono soffocare in assenza di aria.
Tossicologia:
  L’idrogeno non è tossico!.
  In alte concentrazioni, narcotico e soffocazione dovuta ad assenza di ossigeno.
  La voce umana raggiunge toni alti a causa delle modifiche nella velocità del suono.
    Questo effetto, come gli effetti narcotici, scompaiono quando la persona viene portata all’aria rfesca.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Under normal circumstances
  No open fire
  Respect procedures recommended by the operating manual or instructions for handling. If in doubt, better flood system with inert gas before operation!
  Use only certified spares
  Do not open joints under pressure!
  Open valves slowly.
  Do not take any chance when handling combustible gasses and liquids.
Notice: Disrespect of danger does not result in safety!
Contact to hydrogen can cause embrittlement of materials. This is particularly the case in metals crystallizing in Body Centered Cubic crystal lattices (e.g. ferritic steel) which are sensitive to decohesion by interaction with atomic hydrogen. Metals crystallizing in a Face Centered Cubic crystal lattice (e.g. austenitic stainless steel, Al, Ni) are not sensitive. See: DIN 17440 „Stainless steel; and DIN 17102; weldable steels.“
Materials not suitable for Hydrogen Installations:
  Ductile cast iron, Palladium-Titanium-Zirconium
  PVC Tubing-Fittings
  Rubber mixtures
  A-Lock Joints larger than ND 25
Materials suitable for Hydrogen Installations:
  Stainless steel, copper partly steel-alloys
  Welded joints orbital resp. TIG-welding
  Brazed joints
  Locking ring joints e.g. VCR
  Flanges using slot and tongue joints
  Metal-metal sealings conical joints
  Stainless steel tubing
  Perbunane analytical tubing

## Slide 21: Stoccaggio dell‘idrogeno
Stoccaggio
  Un pacco bombole di idrogeno con più di 6 serbatoi non deve essere stoccato all’interno dell’edificio dove si lavora.
  Rifornire piccoli cilindri/recipienti da serbatoi ad alta pressione non è consentito al di fuori di una stazione di rifornimento certificata.
  In caso di dubbio, rifornire taniche/cilindri con gas inerte.
  Ad una pressione residua di < 0,5 barabs è richiesta l’inertizzazione.
  Gli incidenti più frequenti sono:
  Perdite che causano incendi ed esplosioni.
  Rotture di componenti.
  Operazioni non corrette (errore umano).
Importante:
Perdite e operazioni non corrette causano l’ 80 - 90% di tutti gli incidenti
I
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Storage and use of hydrogen from pipes using valves, pressure reducers or other joints are a potential source of leakage. Gas-tightness of pipes, joints or valves should be verified on a regular basis e.g. by using a leak test fluid.
It is highly recommended to use of filling systems which avoid or minimize the release of hydrogen e.g. by self sealing joints.
Incase hydrogen needs to be released or vented the design of the venting lines should make sure that they are:
  balanced and resistant to pressure surge
  take the possibility of detonations into account
  Avoid penetration of impurities and freezing
Protection of installations against excess of permissible pressure should be provided by appropriate safety measures (e.g. safety valve or bypass valves)
In order to avoid sources of leakage, pipes should be welded, brazed, connected by flanges or screw connectors
  Welded or brazed joints are recommended
  Minimization of the number of screw connectors
  Electric contact within the piping system required
Hydrogen must not be used to substitute compressed air
  to empty vessels or piping
  for pressure testing of vessels or piping
  As an gas buffer for liquids inside vessels or drums
  There are exemptions for vessels or piping intended for operation under hydrogen
Hydrogen must not be used to fill balloons (e.g. as toys of for PR-use)

## Slide 22: Instruzioni per maneggiare l‘idrogeno
In caso di incidente:
  Mantenere la calma! Non reagire in modo esagerato.
  Chiudere l‘alimentazione di gas (da una distanza/posizione di sicurezza).
  Attenzione: l’idrogeno brucia con una fiamma incolore e non irradiante.
  Spegnere il fuoco solo se c’è immediato pericolo per le persone o le installazioni.
    Nel caso in cui l’idrogeno può bruciare in modo sicuro, è meglio lasciarlo bruciare per prevenire la formazione di miscele infiammabili.
    Agente che può spegnere le fiamme: polvere, CO2, acqua (rispetto ambiente, es. installazioni elettriche).
  Raffreddare i contenitori di gas pressurizzato ad esempio spruzzando acqua (da distanza di sicurezza).
  Evacuare aree in pericolo.
  Rimuovere le fonti di accensione.
  Avvisare i vicini, mettere in salvo le persone ferite, avvisare i vigili del fuoco.
Le sostanze infiammabili non devono rimanere nella zona di sicurezza.
  Regola empirica: 2 metri in tutte le direzioni.
In caso di dubbio, agire secondo le norme della sicurezza e del piano di emergenza disponibile sul posto.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
The documents shown below are a recommendation from the German “Technical Rules for Compressed Gasses” (TRG406, appendices 6 and 7). They are describing safety instructions as well as an emergency and alarm plan for gaseous fuel vehicle filling stations.

## Slide 23: Esplosione-Protezione
Misure da evitare o dichiarazione di pericolo di esplosione.
Misure tecniche:
  Ventilazione sufficiente (effetto diluizione).
  Rilevazione di concentrazione di idrogeno.
  Certificazione che l’installazione è a prova di perdite.
  Materiali, guarnizioni, giunzioni soggette a test di tenuta (meno di 10-2 a 10-6 mbar/sec (l/sec).
  Preferire saldatura/ brasatura ad attacchi a vite.
  Usare tubazioni solo quando assolutamente necessario.
Misure amministrative:
  Test periodici sulle perdite.
  Manutenzione preventiva.
  Test sulle perdite dopo la manutenzione.
  Manutenzione effettuata solo da personale qualificato. Periodici aggiornamenti dei corsi di formazione per il personale.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Explosion hazard areas according to ATEX:
Are areas where explosion hazard can occur. I.e. a dangerous explosive atmosphere can develop due to local or operational causes.
  Zone 0 Covers areas where a dangerous explosive atmosphere will occur permanently or for a long time. Not applicable to gas handling systems.
  Zone 1 Covers areas, where a dangerous explosive atmosphere occurs occasionally.
  Zone 2 Covers areas where a dangerous explosive atmosphere occurs rarely and only for a short period of time.
In case hydrogen is handled inside buildings or in confined space, the following guidelines for explosion zone declaration are given depending on the status of building ventilation:
Natural Ventilation
  Zone 1: 3 m radius spherical
  Zone 2: additional 6 m
Technical ventilation
  Zone 1: 1 m radius spherical
  Zone 2: additional 3 m
Suction close to the object
  Zone 1: none
  Zone 2: close range
Including alarm system including automatic trigger of safety measures
  Zone 1: close range according to ATEX
  Zone 2: none
“Technically leak proof” permanently guaranteed by construction
  none

## Slide 24: Misurazioni elettriche in Ex-Zones
Non intervenire mai su installazioni elettriche e non usare mai attrezzature di misurazione senza certificazione conforme alla norma ATEX in zone 0-1-2.
In Germania:
  Rispettare la norma VDE 0165 che tratta delle attrezzature elettriche in ambiente esplosivo.
  Definire le “Ex-areas” in conformità alle norme TRB 610.3.2.3.3.1 e 4.2.1.12, così come alle TRG 280 5.3.2 and 8.2.
  Tenere ogni installazione o attrezzature senza “EX-certification” fuori dalle zone 0-1-2.
Generale: usare solo sensori resistenti alle esplosioni.
Ogni computer portatile, telefono cellulare, lampada, ecc. senza protezione dalle esplosioni sono vietati.
B
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
Exemptions to the rules mentioned above can only be granted by the responsible person running the installation. (to be defined in an explosion protection document). The following procedure shall be followed:
  Measurement of H2-content in the atmosphere of the measuring device by a certified person. The measured H2 concentration must be less than 0,8 vol% (20% Lower explosion limit)
  Continuous surveillance during work with online documentation!
  Upon concentration increase to 2 vol% (50% lower explosion limit): leave Ex-Zone immediately.
Place electrical installations, equipment and measurement devices at an easily accessible location.
  In Germany: observe DIN VDE 0100.0165, 0185, 0800, and ATEX rules
  Use explosion proof cables and sensor lines, connect to proper grounding!
Please note: Electrical installations should always be carried out by certified personnel. Ask for certificates and documentation!
Potential equalization, lightning protection
  Measures for internal lightning protection are required. (In Germany, this requirement is fulfilled as soon as potential equilibration according to DIN VDE 0165 is established.)
  In Germany: Carry out potential equilibration according to DIN VDE 0165 as well as DIN VDE 0185
Sparks resulting from static electricity can be a source of ignition. Therefore, the floor resistivity and resistivity of floor covering in an installation need to be respected.
  Potential equalization during temporary installations not always possible. (Use appropriately conductive shoes!)
  Stationary installations in explosion prone areas:106Ohm (in Germany according to DIN 51953 and ZH 1/200)

## Slide 25: Lavorare usando stazioni di rifornimento mobili
Le seguenti misure devono essere osservate, oltre a quelle di protezione dalle esplosioni.
Rimozione sicura di gas combustibili attraverso linee di ventilazione, linee di sicurezza, e linee di fuga (valvole di sicurezza).
Minimo 3 m sopra il pavimento e minimo 1 m sopra il bordo di installazione.
Non condurre linee di fuga sotto il tetto o attici.
Zone di sicurezza che circondano gli scarichi di fuga delle linee di ventilazione:
  Sferica di 1m di raggio (Zona 1).
  Sferica di 3m di raggio forma conica fino al limite più alto (Zona 2).
I
Notes: H2 Training Manual
30.07.26
© ... - For requests: ludwig.joerissen@wbzu.de
Page <number>
10 rules concerning the transport of hydrogen in small vessels, within German GGVS-limit with ordinary vehicle
  During transport of H2-cylinders smoking is absolutely prohibited
  Leak test filled vessels using leak spray.
  Remove Pressure reducer, cap all connectors with sealing caps .
  Always provide proper ventilation. If possible: open window. Do not use recirculating ventilation.
  Fix cylinder/container inside vehicle. Best to the floor.
  Do not transport H2-containing vessel in sealed packing.
  Do not heat H2-containing vessels above 50°C, e.g. above heating channels. Protect from direct irradiation from the sun.
  If leaks are suspected, immediately remove vessel from vehicle. Warn people passing by. Proceed according to safety sheet.
  In case of an accident with subsequent fire hazard, remove H2-vessel. Inform rescue personnel about H2-vessel if it still remains within the vehicle. Hand over instructions for accident and safety sheet “compressed hydrogen”.
  After completion of journey, remove H2-vessel from vehicle. Do not leave vessel unattended during transport. Do not store in private garages.